## Slide 1: INSTALLING DISINFECTION SYSTEMS
Notes: <number>
<number>
This section will cover installation of disinfection systems in the treatment train.

## Slide 2: CIDWT disclaimer
These materials are the collective effort of individuals from academic, regulatory, and private sectors of the onsite/decentralized wastewater industry. These materials have been peer-reviewed and represent the current state of knowledge/science in this field. They were developed through a series of writing and review meetings with the goal of formulating a consensus on the materials presented. These materials do not necessarily reflect the views and policies of the Consortium of Institutes for Decentralized Wastewater Treatment (CIDWT). The mention of trade names or commercial products does not constitute an endorsement or recommendation for use from these individuals or entities, nor does it constitute criticism for similar ones not mentioned.
Notes: <number>
<number>
The training materials we will be using for this program were developed by the Consortium of Institutes for Decentralized Wastewater Treatment. These materials were developed using a stakeholder process where industry professionals conducting service of onsite wastewater treatment systems were assembled to describe their activities, provide input on material development and develop the operational checklists utilized to assess the operational status of the components. The writing team, consisting of members of the Consortium of Institutes for Decentralized Wastewater Treatment, developed the materials with the review by the industry.
We do not endorse any products or commercial services mentioned in these materials or during the presentations. Nor does it constitute a criticism for similar products or commercial services not mentioned.

## Slide 3: NDWRCDP disclaimer This work was supported by the National Decentralized Water Resources Capacity Development Project (NDWRCDP) with funding provided by the U.S. Environmental Protection Agency through a Cooperative Agreement (WPA No. X-830851-01-0) with Water Environment Research Foundation (WERF) in Alexandria, Virginia. These materials have not been reviewed by the U.S. Environmental Protection Agency, NDWRCDP, or WERF. The contents of these materials do not necessarily reflect the views and policies of the NDWRCDP, WERF, or the U.S. Environmental Protection Agency, nor does the mention of trade names or commercial products constitute their endorsement or recommendation for use.
Notes: <number>
<number>
The development of these materials was partially supported by the National Decentralized Water Resources Capacity Development Project through a grant from the U.S. Environmental Protection Agency through the Water Environment Research Foundation. These organizations have not reviewed these materials.
Again, the mention or absence of any products or commercial services does not constitute an endorsement or recommendation for these products or services.

## Slide 4
Introduction - what we will cover :
Overview of disinfection
Types of disinfection systems
  Chlorination
  Ultraviolet light
Placement in the treatment train
Basic components
Installation steps – housing, electrical, controls
Manufacturer installation specs
Startup measures
Notes: <number>
Self explanatory

## Slide 5: Disinfection overview
Destruction or inactivation of disease-causing organisms
Reduces concentration of pathogenic organisms to an acceptable level
Relates to a health standard
Notes: <number>
If soil does not have the capacity to reduce pathogens in the wastewater, disinfection can fulfill part of that and may be an option.
Some organisms are resistant to certain disinfection techniques. Therefore, we may NOT achieve complete sanitization. Typically the treatment goal is to lower concentrations to levels that do not cause environmental or public health problems.

## Slide 6: Types of disinfection systems
Chlorination
  Used only with advanced treated effluent
  Strong oxidizing agent
  Highly corrosive
  Passes through cell wall – kills organism
  Contact time and concentration is important
Dechlorination
  Remove residual chlorine
  Protect receiving environment
  Not often used
Notes: <number>
Disinfection by chlorination is effective when used on advanced treated wastewater that has a level of 30 mg/L of BOD AND TSS or less. With higher concentrations of BOD and TSS, disinfection is limited by organic matter in wastewater. Chlorination should not be used with straight septic tank effluent.
Systems may use tablet or liquid chlorinators (more on this in later slides).
Contact time and the concentration of organisms in wastewater are important factors determining effectiveness of chlorination. Short contact times reduce kill rates, and very high concentrations of organisms challenge the treatment process.
A treatment train may not have a dechlorination (dechlor) unit. This really depends on the regulatory requirements and/or sensitivity of the receiving environment. It is quite possible to have a chlorination unit and not have a dechlorinator.
For all practical purposes, dechlor units look very similar to chlorination units – the only functional difference is the type of chemicals that are used in each unit. This will be explained later.
Again, it is important to note that some organisms may be resistant to chlorine.

## Slide 7: Types of disinfection systems (cont.)
Ultraviolet (UV) light
  Used only with advanced treated effluent
  Electrical current passing through a special lamp creates UV light
  UV light destroys organism DNA / cells
  Clarity of wastewater is important
  Contact time is important
    Flow rate through unit
Notes: <number>
How it works – UV light disrupts the organism’s DNA.
UV light is the same wave length of light that give humans skin cancer by mutating our DNA or cells. We can shield ourselves from UV rays by hiding under a beach umbrella or by putting on sun screen which serves as a barrier to UV ray penetration.
Cloudy wastewater provides a shield that prevents UV light from contacting microbes, essentially acting like a beach umbrella for the microbes. Wastewater low in BOD and TSS is needed for good UV light kills. Contact time is also needed for the UV reaction to be effective.
If the flow rate is too high, there will be short contact times, and less time for disinfection to be effective.

## Slide 8
Typical placement of a disinfection system in a treatment train
Disinfection
technology
Notes: <number>
Disinfection be placed in the treatment train after advanced treatment technologies, to assure that BOD and TSS concentrations in effluent are low (< 30/30 mg/L). If wastewater has a high(er) organic loading then disinfection agents do not penetrate well - the light refracts, or the microorganisms are hidden within or behind the organic particles. This lowers the effectiveness of the disinfection process; the microbial kill isn’t as efficient.
If a dechlorination unit is required in the design, then it would be placed immediately after the chlorinator unit in the treatment train.

## Slide 9: Basic components of a external tube tablet chlorination system (not for direct burial)
Housing
Notes: <number>
The upper portion of the chlorine tablet feed tubes are outside the chlorinator housing, and the bottom portion extends into the housing unit. The feed tubes are not sealed to the housing unit, so this connection is not watertight. As a result, external tube units are usually placed within an open area, or inside a access box or manhole, and are NOT directly backfilled with soil.
Tablet chlorinators generally have four components:
  Chlorine tablets.
  A tube that holds the tablets.
  A contact device, which puts the chlorine tablets into contact with the wastewater.
  A contact chamber, a separate contact device or more typically a down stream pump tank where the treatment wastewater is stored before it is distributed. Some units have a small integral contact device (or area) at the base of the unit, but this is usually not a sufficient contact chamber to provide adequate time for chlorine to react with wastewater.

## Slide 10: Internal feed tube tablet chlorinator
Feed tubes are inside the enclosure or housing unit
Backfill is not directly against the feed tubes
Unit is watertight
Notes: <number>
Internal feed tube type chlorinators provide more damage protection because feed tubes are protected by the walls of the unit.
Backfill material does come in direct contact with the outside walls of the unit, but not the feed tubes.
The housing unit should be designed to be watertight.
Take care that compaction methods do not damage the enclosure unit.

## Slide 11: Tablet chlorination
Tablet chlorinators often have 4 components
  Chlorine tablets
  Tube that holds tablets
  Contact device
    Puts tablets in contact with wastewater
  Contact chamber
    Usually a down stream pump tank where water is stored before it is distributed
Notes: <number>
Tablet chlorinators often have 4 components.
  The chlorine tablets
  A tube that holds tablets
  A contact device that puts tablets in contact with wastewater
  A contact chamber. This is usually a down stream pump tank where water is stored before it is distributed

## Slide 12: Liquid chlorinator system
Metering done by either a vacuum or pump
Notes: <number>
A liquid chlorination system consists of a bleach solution contained in mixing tank. A metering pump doses bleach into wastewater stream. This may be a peristaltic pump or an aspirator.
As with the tablet chlorination system, there must be a downstream contact chamber where wastewater and bleach can mix.

## Slide 13: Chlorine contact chamber
Chamber where chlorinated wastewater is temporarily stored
  Allows contact time
Placed after chlorinator
Must be watertight
Notes: <number>
Some designs call for a separate contact chamber.
A pump tank (used for final dispersal) can be the designated contact chamber.
A 30-minute contact time is needed.
Most chlorinators have a small contact zone incorporated in the housing unit, but that is not large enough to serve as a contact chamber.

## Slide 14: Installation of disinfection devices
Chapter 10.
Form 10.9 installation checklist: disinfection – chlorine
These are basic installation steps
Always check the manufacturer's installation materials for technology specific tasks and details
Notes: <number>
This sets the stage for the part of the presentation that deals with the installation form itself. Have audience turn to the disinfection checklist in their manuals.
This manual can not address all the installation nuances for every technology on the market. The installer should always seek out manufacturer training and follow vendor supplied materials for specific tasks and details.

## Slide 15: Similar installation steps -
Excavating for the unit
Hole depth elevation
Firm base
Unit is level and plumb
Backfilling / compaction
Electrical power supply
Similar to techniques used for tanks, piping, media filters, and ATU installations.
Notes: <number>
Installation steps such as excavating for the disinfection unit, the depth and size of the hole, firm base, placement of the housing unit so that it is level and plumb, backfilling and compaction, and bringing in electrical power are similar installation techniques that have been talked about for tanks, piping, media filters and ATUs. Because these steps are familiar, we won’t dwell on them, only mention them briefly.

## Slide 16: 1. Type of chlorination system
Manufacturer: chlorinator___ dechlorinator___
Model # of chlorinator:____
Model # of dechlorinator:____
Method:
Tablet
Liquid
Use separate form if dechlorinator is
also installed
Notes: <number>
This info is important as it helps define the system, and makes the installer aware that manufacturer installation instructions are likely to exist, and should be followed.

## Slide 17: 2. Enclosure
Unit should be:
a. Level and plumb
b. Stable
Watertight
Placed in pump chamber
e. Set on a compacted base
Notes: <number>
The disinfection unit is often placed within the down gradient pump tank, where it is protected, stable, and not subject to soil settling or shifting.
If installing a direct burial unit between an advanced treatment unit and a pump tank, then the chlorinator unit location could be on excavated soil. If this is the case, then proper soil bedding, compaction and stabilization needs to take place.

## Slide 18: 2. Enclosure (cont.)
f. Bedding material used:______
Backfill free of large stones
Notes: <number>
Follow the manufacturer’s instructions.

## Slide 19: 2 h - j. Enclosure
Tablet feed tubes /reservoir extend above grade
Access caps are secure
Ground surface graded to shed water away from unit
Notes: <number>
The photo shows tablet feed tubes extending above grade. Liquid chlorinator access covers should come above grade too. All access risers should be secured for safety.

## Slide 20: 3. Injection device – liquid chlorinator (if applicable)
Method:
  Vacuum / suction
  Pump
  Venturi
Connections properly sealed and watertight
Electrical conduit, splice or junction box installed
Cord grips tightened
Splice box lid(s) tightened
Control panel and controls installed
Notes: <number>
Much of this will typically be done by the electrical contractor, but the installer may want to look over the contractor’s shoulder.
Check local codes.
Total bends in degrees should not exceed 270o. Install splice and junction boxes so they are accessible for O&M.
Backfill carefully and compact to prevent conduit deflection and damage.
Use expansion joints and seals.

## Slide 21: 4. Chlorine contact chamber
Integral with component
  No extra work
Separate chamber
  Install in a similar manner
Subsequent pump tank
  Use same installation measures as other tanks
Must be watertight
Notes: <number>
Self explanatory

## Slide 22: 5. Manufacturer’s required installation procedures followed?
If applicable, include manufacturer installation checklist in your files
Notes: <number>
Self-explanatory

## Slide 23: Startup checklist – chlorine
Most of this is a simple verification and check-off process
Notes: <number>
This is the beginning of chlorine startup checklist. In many cases this is a simple verify and check-off process.

## Slide 24: 1. Type of chlorination system
Manufacturer: chlorinator___ dechlorinator___
Model # of chlorinator:____
Model # of dechlorinator:____
Method:
Tablet
Liquid
Notes: <number>
This information is important as it helps verify and define the system, and makes the installer aware that manufacturer installation instructions are likely to exist, and should be followed.

## Slide 25: 2. Startup – tablet chlorinator
Chlorine tablets in place
  Yes
  No
  NA
Tablets come in contact with effluent
Number of tablets added at start up _____
(only add 3 – 5 tablets)
Notes: <number>
Verify that tablets are added and in contact with effluent.
ONLY ADD BETWEEN 3 TO 5 TABLETS. Record the number of tablets added to tubes.
You don’t want tablets setting in the feed tube for a long time, as they absorb moisture and swell and won’t fall into place as the lower tablet erodes away. Swelled tablets are hung up in feed tube and not in contact with wastewater.

## Slide 26: Chlorine precautions
Calcium hypochlorite
  Use Ca(OCl)2 for wastewater applications
  Strong oxidizing agent
Wear protective gloves and eye wear
Avoid breathing chlorine gas
Open container in well ventilated conditions
Note wind direction when opening units
Do not store chlorine in house or shop
  Corrodes steel and electrical connections
Don’t forget MSDS for all chemicals you handle!
Notes: <number>
Caution the installers to always have appropriate material safety data sheets (MSDS) for all chemicals they carry.
Chlorine is a strong oxidizer – gas is harmful to breath. It will also corrode steel and electrical connection, so store in suitable location.

## Slide 27: Chlorine precautions
DO NOT use swimming pool chlorine for wastewater applications
DO NOT mix swimming pool chlorine tablets with wastewater tablets
DO NOT allow tablets to come in contact with oil / petroleum products
Explosions and fire hazard
Notes: <number>
Caution the homeowner to not store chlorine in the house.
Always use caution when handling chlorine products and use the correct product.
Wastewater tablets are composed of calcium hypochlorite, which is a basic (high pH) material.
Swimming pool tablets (Trichlorocyanuric acid) are acidic material.
Do not mix acids and bases together as explosions may occur.

## Slide 28: 3. Startup – liquid chlorinator
Chlorine present in reservoir
  Percent chlorine in solution
Injection method:
  - Vacuum/suction
  - Pump
  - Venturi
Injection device operating correctly
  Method used: ________
Notes: <number>

## Slide 29: 3. Startup – liquid chlorinator
d. Dose volume confirmed Amount _______
e. Proper mixing occurring Y/N
f. Operating switch set to
  ON or AUTO (only for pumps)
reservoir
aspirator
Notes: <number>
To check the correct dose volume:
With an aspirator – mark the liquid level in the reservoir, and then look at drop in level. The aspirator sucks chlorine solution out of the reservoir as flow passes by end of aspirator hose.
With a pump – collect the liquid when the pump doses.

## Slide 30: 4. Tablet dechlorinator
Required
NA
Dechlorination tablets in place
  Chemical composition: __________________
  (should be sodium bisulfate)
Tablets in contact with effluent Y / N
Number of tablets added at start up _____
(3 to 5 maximum)
Notes: <number>
Dechlorination may not be required.
Sodium bisulfate tablets are used for dechlorination.
Tablets must be in contact with wastewater.
Indicate how many tablets were added. Add no more than 3 to 5 tablets.

## Slide 31: 5. Contact chamber
Note location in treatment train
Integral with component
  No extra work
Separate chamber
  Install in a similar manner
Subsequent pump tank
  Use same installation measures as other tanks
Must be watertight
Notes: <number>
Self explanatory

## Slide 32: 6. Manufacturer’s required startup procedures followed?
If applicable, include manufacturer startup checklist in your files
Notes: <number>
Self-explanatory

## Slide 33: UV light installation
These are basic installation steps
Always check the manufacturer's installation materials for technology- specific tasks and details
Notes: <number>
The manufacturer will typically have installation procedures that need to be followed to remain within warrantee.

## Slide 34: Basic components of a UV disinfection system
Housing – slides or threads onto a pipe end
Removable lamp
Replaceable ballast
Quartz or Teflon protective sleeve
Watertight electrical splice box
Electrical controls located in a panel box
Notes: <number>
All these components need to be installed. The UV disinfection system comes as a unit.
Wastewater flows down one side of UV lamp and up along other side. This particular one is configured similarly to a “P” trap.
The ballast unit is NOT shown in the figure. The ballast is sensitive to cold temperatures – check manufacturer recommendations for cold weather installations.

## Slide 35: UV light precautions
UV radiation can cause serious injury
to unprotected eyes
  similar to a welding burn
Never look directly at UV lamp while
power is on
Use proper UV-rated safety glasses
when energy is supplied to unit
Notes: <number>
Self explanatory

## Slide 36: 1. Component description
Manufacturer: _____ Model #: _____
Flow rating: _____ PDR: _____ (if pressure)
Dosing method:
  Pressure dosed
  Gravity fed
Notes: <number>
This checklist documents basic information. If the flow rating is exceeded then microbial kill will not be effective.

## Slide 37: 2. Housing installation
Location:
  Buried
  Within a tank (best)
  Other
Unit stable
Unit level / plumb
Notes: <number>
Picture above is of UV unit located inside a 24 inch PVC soil treatment area pump basin.
This unit has a pitless adaptor type of fitting where UV assembly attaches to influent pipe with a slip “O” ring seal.
Some units may come with a quick disconnect, or a threaded union.
Housing is sturdy, but installer still needs to be careful to not abuse the unit.
IF UNIT IS A DIRECT BURIAL, located between the advanced treatment unit and the pump tank or STA, then UV unit may be located on excavated ground. Proper bedding, compaction, and stabilization would be needed. Consult the manufacturer.

## Slide 38: Housing installation
UV housing unit cast in place in pump tank
Installer installs internal components & makes water-tight glue seal to unit
Notes: <number>
Some manufacturers have worked with local tank precasters to have UV units molded into inlet end of pump chambers used to dose soil treatment areas. A riser extending to finish grade (with a secured lid) is used around the exposed upper portion of the unit. This should have both a watertight connection to the tank top, and a watertight lid to provide access for O&M.

## Slide 39: 2. Housing installation (cont.)
Protected from freezing, heat, dust, vandals
Unit watertight (check at startup)
If buried
  Compacted base
  Bedding material used ________
Grab handle needed and secure - PVC T-handle attached to UV lamp housing
Notes: <number>
Self explanatory

## Slide 40: 3. Electrical conduit, splice or junction box(es)
Installed for UV unit and controls
Sealed and watertight penetrations
Adequate cable length provided for servicing unit
Cord locks tightened
Splice box lids tightened
Notes: <number>
Do not over tighten cord locks; they can cut through outer cable sheathing and moisture can enter and wick along inside of cable, resulting in corrosion.
Tight junction / splice box lids will help keep out moisture, which will minimize corrosion risks. As corrosion builds on electrical connections, electrical resistance increases, and this lowers voltage (power) to UV unit.

## Slide 41: 3. Electrical conduit, splice or junction box(es)
f. Power supply
  AC (typical)
  DC
  Voltage ________
GFCI protected circuit
  Use for safety
Notes: <number>
Most use AC household current.
Always use a ground fault circuit interrupter (GFCI) protected circuit.
Consult the manufacturer for length of conductors, so that voltage drops do not occur.

## Slide 42: 4. Controls
Panel manufacturer: ________ Model: ______
Telemetry present:
  Yes
  NA
  Type:___________________________
  Owners advised about telemetry
    Yes
Notes: <number>
Someone needs to discuss the telemetry feature with the system owner, ideally during the planning stage.
ON vs. OFF choice is determined by whether system is going to be used now.

## Slide 43: 5. Manufacturer’s required installation procedures followed?
If applicable, include manufacturer installation checklist in your files
Notes: <number>
Self-explanatory

## Slide 44: Startup checklist form 10.12 - ultraviolet light
Notes: <number>

## Slide 45: 1. Manufacturer and model #
We are verifying what was just installed
All answers on form should be “yes”
If not, then:
  Contact designer
  Contact regulatory official
  Correct the No
Notes: <number>
The start up is a simple check-off to verify what was installed.
ALL answers should be YES on this form.

## Slide 46: 2. Housing assembly installation
Unit level /plumb (answer Yes or No for each)
Unit stable
Unit accessible
Grab handle needed and installed
Watertight and no leakage at quick disconnect
We are verifying what was just installed
Notes: <number>
ALL answers should be YES. If not, correct the “No”, and /or contact designer and regulatory official.

## Slide 47: Housing unit installation
f. Provides protection from:
  Freezing
    Insulation adequate
  Excessive heat (lowers lamp life)
  Dust (lowers lamp life)
  Vandalism
Notes: <number>
The housing unit provides important protection for UV units.

## Slide 48: Power supply
Type of power
  AC
  DC
  Voltage at lamp: _______
Power supply appropriate for unit
  GFCI operable
UV lamp operable
Indicate lamp replacement period
  12 month
  24 month
  Other: _______
Lamp accessible
Adequate cable slack present
Splice box lid, cord grips tight
Notes: <number>
GFCI is used as a risk prevention measure. Installer should check that the GFCI is functioning.

## Slide 49: 4. UV control panel
Unit equipped with a lamp intensity sensor Y/N
  Type of sensor
    Current
    Lamp intensity meter Record reading ____
    Photocell
Alarm present
  If so, operating properly Y/N
GFCI operating Y/N
Enclosure watertight Y/N
Current sensor normal
reading about 0.28
Notes: <number>
Self explanatory

## Slide 50: 4. UV control panel
e. Alarm test switch operating properly Y / N
f. Control switch set to:
  ON
  OFF
g. Telemetry unit connected and operable Y / NA
  Land line phone service active
  Owner(s) advised about telemetry operation
Notes: <number>
Advise the owners about telemetry operation.

## Slide 51: 5. Manufacturer’s required startup procedures followed?
If applicable, include manufacturer startup checklist in your files
Notes: <number>
Self-explanatory

## Slide 52
What we covered
Overview of disinfection
Types of disinfection systems
  Chlorination
  Ultraviolet light
Placement in the treatment train
Basic components
Installation steps – housing, electrical, controls
Manufacturer installation specs
Startup measures
Notes: <number>

## Slide 53: Are there any questions about installing disinfection units?
Notes: <number>