## Slide 1: OUTFALLS
Notes: <number>
The section discusses outfall systems and their installation

## Slide 2: CIDWT disclaimer
These materials are the collective effort of individuals from academic, regulatory, and private sectors of the onsite/decentralized wastewater industry. These materials have been peer-reviewed and represent the current state of knowledge/science in this field. They were developed through a series of writing and review meetings with the goal of formulating a consensus on the materials presented. These materials do not necessarily reflect the views and policies of the Consortium of Institutes for Decentralized Wastewater Treatment (CIDWT). The mention of trade names or commercial products does not constitute an endorsement or recommendation for use from these individuals or entities, nor does it constitute criticism for similar ones not mentioned.
Notes: <number>
<number>
The training materials we will be using for this program were developed by the Consortium of Institutes for Decentralized Wastewater Treatment. These materials were developed using a stakeholder process where industry professionals conducting service of onsite wastewater treatment systems were assembled to describe their activities, provide input on material development and develop the operational checklists utilized to assess the operational status of the components. The writing team, consisting of members of the Consortium of Institutes for Decentralized Wastewater Treatment, developed the materials with the review by the industry.
We do not endorse any products or commercial services mentioned in these materials or during the presentations. Nor does it constitute a criticism for similar products or commercial services not mentioned.

## Slide 3: NDWRCDP disclaimer This work was supported by the National Decentralized Water Resources Capacity Development Project (NDWRCDP) with funding provided by the U.S. Environmental Protection Agency through a Cooperative Agreement (WPA No. X-830851-01-0) with Water Environment Research Foundation (WERF) in Alexandria, Virginia. These materials have not been reviewed by the U.S. Environmental Protection Agency, NDWRCDP, or WERF. The contents of these materials do not necessarily reflect the views and policies of the NDWRCDP, WERF, or the U.S. Environmental Protection Agency, nor does the mention of trade names or commercial products constitute their endorsement or recommendation for use.
Notes: <number>
<number>
The development of these materials was partially supported by the National Decentralized Water Resources Capacity Development Project through a grant from the U.S. Environmental Protection Agency through the Water Environment Research Foundation. These organizations have not reviewed these materials.
Again, the mention or absence of any products or commercial services does not constitute an endorsement or recommendation for these products or services.

## Slide 4: What’s ahead
Definition of outfall
Installation
Startup

## Slide 5: Outfalls
Used to discharge from
  Sump pump
  Curtain, interceptor, or perimeter drains
  Advanced treatment systems
    Only for highly treated effluent
High risk
  Potential for direct human contact with wastewater
Notes: <number>
Outfalls are most commonly used for discharge from a sump pump, or water collected from curtain, interceptor, or perimeter drains. In a few instances, they are utilized after highly treated effluent has been generated by advanced treatment systems.
Systems using these are higher risk due to the potential for direct human contact with wastewater. They often require a permit and have strict sampling requirements.

## Slide 6: Discharging system
Discharge pipe delivers directly to a waterway, road ditch, or ground surface.
Effluent must be able to exit the system.
Notes: <number>
These systems utilize a discharge pipe delivering the water directly to a waterway, road ditch, or ground surface on the property. In a discharging system the point is to move the water through the pipe.

## Slide 7: Installation steps
Form 11.9 installation checklist: outfalls
Notes: <number>
Please follow along on page 11-71 of your manual with Installation Checklist 11.9- Outfalls.

## Slide 8: 1. Outfall specifications
Record effluent source
Where is water discharged?
Is permit required?
Notes: <number>
Some general information about the outfall should be recorded. Document the source of the effluent being discharged. Keep in mind that the source should be generating high quality discharge. Indicate where the outfall is discharging and whether or not a permit for discharge is required.

## Slide 9: 2. Site preparation
Stake the outfall location
Verify elevations
Confirm horizontal setbacks
Notes: <number>
The first step in site preparation is to stake the outfall location. Verify the elevation difference between the outfall and the preceding component’s outlet. The end of the outlet pipe should be at the lowest elevation in the treatment train. Confirm the horizontal setbacks required by local code have been meet or surpassed.

## Slide 10: 3. Excavation
Document means of excavation
Trench bottom
  Dry, free of rocks and debris
  Graded as specified in the design
Notes: Previous presentations have discussed proper excavation techniques. Document the equipment or means of excavating the outfall. The bottom of the excavation should be free of water and graded as specified in the design.
<number>

## Slide 11: 4. Outfall installation
Pipe size
Bedding material
Erosion prevention
Document side and pool specifications
Protect from animal activity
Notes: <number>
Document the pipe size used for the outfall. Indicate the material used for the bedding/foundation under the pipe. The outlet must be stable. Be sure that the location will not have problems with erosion due to water flowing from the outfall. Document the side and pool protection specifications. The discharged effluent must be protected from animal activity.

## Slide 12: 5. Sampling port
Should be installed if sampling is required
Notes: <number>
Most outfalls require regular collection of samples on a regular basis. If the system permit requires sampling then there must be a sampling device installed. Document the installation of a sampling device and give a brief description of it. The sampling port shown on this slide is a good example of what you’d want. The wastewater collects in the vertical pipe and since wastewater is constantly flowing through it, a composite sample can be collected.

## Slide 13: Startup
Verify Installation details
Outlet unobstructed
Vegetation managed
Discharge pipe in good condition
Accessible for O&M
Notes: <number>
The startup verifies proper installation. In addition, you must ensure the area around the outfall is stable. The outlet of the outfall structure should be free of obstructions. There should be no vegetation blocking the outlet which could cause plugging and backing up of the system. Water must be able to flow freely from the pipe. The outfall pipe should be in good condition and accessible for sample collection and other O&M.

## Slide 14: Summary
Outfall
  Potential for human contact!
  Should be highly treated before discharge
  Often requires sampling
Installation
Startup
Notes: Outfall has a high potential for human contact! Effluent should be highly treated before discharge, and sampling is often required to assure safety.